Technical Glass Products has included notes in this specification to assist you in tailoring the content to your project.  These comments will appear on your screen in blue.  To hide them and view only the specification, do the following:

Click the “Office” button and then click the word “Options” OR select the “File” and then click “Options”.   Click “Display” at the left of the dialog box.  Remove the check mark from the “Hidden Text” box.  Then click “OK.”  All blue text will then be hidden.

This document is designed for use by a qualified construction specifier. Proper modifications are required to tailor this specification to your project needs.  Optional text is placed between brackets “[ ].”  Blank underlines “__” represent areas you need to fill in with your project specific information. For assistance, call Technical Glass Products at 1-800-426-0279.

This guide specification is a supplier-specific proprietary product specification using the proprietary method of specifying applicable to project specifications and master guide specifications. Fireframes ClearView System is available with your choice of perimeter frames including Fireframes® Heat Barrier Series (rated for 60 / 120 minutes), Fireframes Aluminum Series (rated for 60 minutes) supplied by Technical Glass Products further described in Part 2 – Products.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Section 08 41 23 - Fire Rated STEEL FRAMED ENTRANCEs and storefronts-FIREFRAMES CLEaRVIEW® SYSTEM

GENERAL

## SUMMARY

Section includes:

Fire rated glazing and framing systems for installation as wall sections in interior openings

Verify that Section titles referenced below are correct for this Project's Specifications; Revise the Section number and title below to suit project requirements, specification practices and section content. Refer to CSI MasterFormat for other section numbers and titles.

Verify other nearby items are specified.

Related Sections:

Section 05 12 00 “Structural Steel Framing:” Steel attachment members

Section 05 50 00  “Metal Fabrications:” Steel attachment members inserts and anchors

Section 07 84 00 “Firestopping:” Firestops between work of this section and other fire resistive assemblies.

REFERENCES

Adjust lists below to suit Project. Specifically this means to delete the types of finish that are not used AAMA 2603 thru 2605 and if the system is used in interior applications all the air and water infiltration testing and standards may be removed.

American Architectural Manufacturers Association (AAMA)

AAMA 2603-2002 - Voluntary Specification, Performance Requirements and Test Procedures for Pigmented Organic Coatings on Aluminum Extrusions and Panels.

AAMA 2604-2005 - Voluntary Specification, Performance Requirements and Test Procedures for High Performance Organic Coatings on Aluminum Extrusions and Panels.

AAMA 2605-2005 - Voluntary Specification, Performance Requirements and Test Procedures for Superior Performing Organic Coatings on Aluminum Extrusions and Panels.

American Society for Testing and Materials (ASTM):

Fire safety related:

ASTM E119:  Methods for Fire Tests of Building Construction and Materials.

Material related

ASTM A 1008/A 1008M - Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength, Low Alloy, and High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable; 2007.

ASTM A 1011/A 1011M - Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy and High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength; 2006b.

Sound related:

ASTM E 90-04: Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements

ASTM E 413-04: Standard Classification for Rating Sound Insulation

American Welding Society (AWS)

AWS D1.3 - Structural Welding Code - Sheet Steel; 2007

Canadian Standards

CAN/ULC-S101 Standard Test of Fire Endurance Tests of Building Construction and Materials

CAN/ULC-S106 Standard Method for Fire Tests of Window and Glass Block Assemblies

National Fire Protection Association (NFPA):

NFPA 251:  Standard of Methods of Fire Tests of Building Construction & Materials

NFPA 257:  Standard for Fire Test of Window Assemblies

Underwriters Laboratories, Inc. (UL):

UL 9:  Fire Tests of Window Assemblies

UL 10 C:  Positive Pressure Fire Tests of Window & Door Assemblies

UL 263:  Fire tests of Building Construction and Materials

American National Standards Institute (ANSI):

ANSI Z97.1:  Standard for Safety Glazing Materials Used in Buildings

Consumer Product Safety Commission (CPSC):

CPSC 16 CFR 120:  Safety Standard for Architectural Glazing Materials

American Society of Civil Engineers (ASCE)

ASCE 7 – Minimum Design Loads for Buildings and Other Structures; 2005

New York City approval

MEA# 242-00-M

      - DEFINITIONS

Manufacturer:  A firm that produces primary glass, fabricated glass or framing as defined in referenced glazing publications.

SUBMITTALS

Submit in accordance with Section <Insert Section #>.

Product Data:

Technical Information:  Submit latest edition of manufacturer’s product data providing product descriptions, technical data, Underwriters Laboratories, Inc. listings and installation instructions.

Shop Drawings:

Include plans, elevations and details of product showing component dimensions; framed opening requirements, dimensions, tolerances, and attachment to structure

Samples (optional):   For following products:

Glass sample-as provided by manufacturer

Sample of frame

Verification of sample of selected finish

Glazing Schedule:  Use same designations indicated on drawings for glazed openings in preparing a schedule listing glass types and thicknesses for each size opening and location.

Warranties: Submit manufacturer’s warranty.

Certificates of compliance from glass and glazing materials manufacturers attesting that glass and glazing materials furnished for project comply with requirements.

Separate certification will not be required for glazing materials bearing manufacturer’s permanent label designating type and thickness of glass, provided labels represent a quality control program involving a recognized certification agency or independent testing laboratory acceptable to authority having jurisdiction.

QUALITY ASSURANCE

Testing Agency Qualifications: Qualified according to

International Accreditation Service for a Type A Third-Party Inspection Body (Field Services ICC-ES Third-Party Inspections Standard Operating Procedures, 00-BL-S0400 and S0401)

International Accreditation Service for Testing Body-Building Materials and Systems

Fire Testing

ASTM Standards  E 119

CPSC Standards 16 CFR 1201

NFPA Standards 251, 252, 257

UL Standards 9, 10B, 10C, 1784, UL Subject 63

BS 476; Part 22:  1987

EN 1634-1

CAN/ULC Standards S101, S106

Installer Qualifications:  An experienced installer who has completed glazing similar in material, design, and extent to that indicated for this Project; whose work has resulted in glass installations with a record of successful in-service performance; and who employs glass installers for this Project who are certified under the National Glass Association Glazier Certification Program as Level 2 (Senior Glaziers) or Level 3 (Master Glaziers).

Delete paragraph above or below.  If retaining above, verify with prospective installers that they can comply with glazier certification requirements.

Installer Qualifications:  An experienced installer who has completed glazing similar in material, design, and extent to that indicated for Project and whose work has resulted in construction with a record of successful in-service performance.

Source Limitations for Glazing Accessories:  Obtain glazing accessories from one source for each product and installation method indicated.

Fire-Rated Wall Assemblies: Assemblies complying with ASTM E119 that are classified and labeled by UL, for fire ratings indicated, based on testing in accordance with UL 263, ASTM E119.

Adjust certification list below to suit Project.

Generally retain paragraph below unless types of glass selected do not require labeling by authorities having jurisdiction or if certification is required as well as labels.

Listings and Labels - Fire Rated Assemblies:  Under current follow-up service by Underwriters Laboratories® maintaining a current listing or certification. Label assemblies accordance with limits of manufacturer’s listing.

Regulatory Requirements:  Comply with provisions of the following:

DELIVERY, STORAGE AND HANDLING

Deliver, store and handle under provisions specified by manufacturer.

PROJECT CONDITIONS

Obtain field measurements prior to fabrication of frame units. If field measurements will not be available in a timely manner coordinate planned measurements with the work of other sections.

Note whether field or planned dimensions were used in the creation of the shop drawings.

### Coordinate the work of this section with others effected including but not limited to: other interior envelope components and door hardware beyond that provided by this section

WARRANTY

Provide the Pilkington Pyrostop® and the [Fireframes® Heat Barrier Series] [Fireframes® Aluminum Series] standard five-year manufacturer warranty.

PRODUCTS

Adjust options in Article below to suit Project. Fireframes ClearView System is available with your choice of perimeter frames including Fireframes® Heat Barrier Series (rated for 60 / 120 minutes), Fireframes Aluminum Series (rated for 60 minutes).

MANUFACTURERS - FIRE RATED  [WALL ASSEMBLY]

Manufacturer Glazing Material:  “Pilkington Pyrostop®” fire-rated glazing as manufactured by the Pilkington Group and distributed by Technical Glass Products, 8107 Bracken Place SE, Snoqualmie, WA  98065 phone (800.426.0279) fax (425.396.8300) e-mail tgp.sales@allegion.com, web site http://www.fireglass.com

Frame System:  [Fireframes® Heat Barrier Series] [Fireframes® Aluminum Series] fire-rated [steel] frame system with a 5 mm vertical butt joint as manufactured and supplied by Technical Glass Products, 8107 Bracken Place SE, Snoqualmie, WA  98065 phone (800.426.0279) fax (425.396.8300) e-mail tgp.sales@allegion.com  web site http://www.fireglass.com

Substitutions:  Substitutions for Glazing Material and Frame System not permitted.

PERFORMANCE REQUIREMENTS

Adjust fire rating minutes in paragraphs below to suit Project.

Fire Rating Requirements

Duration-- Windows:  Capable of providing a fire rating for [60] [120] minutes.

Duration-- Walls:  Capable of providing a fire rating for [60] [120] minutes

Delegated design: For the performance requirements listed below requiring structural design provide data, calculations and drawings signed and sealed by an engineer licensed in the state [province] where the project is located.

Design Requirements

Dimensions – Window/Wall Assembly:

Perimeter framing face dimension:  Head, sill and jamb [Fireframes® Heat Barrier Series-3-1/8-inches] [Fireframes® Aluminum Series – 2 inches]

Horizontal and/or vertical mullions:  [Fireframes® Heat Barrier Series - 4-1/8-inches] [Fireframes Aluminum Series –2 inches] on the face.

Depth of perimeter and mullion: depth varies based on rating and profile

Construction:  Narrow-profile, roll-formed steel architectural grade specialty frames.

MATERIALS - GLASS

Fire Rated Glazing:  Composed of multiple sheets of Pilkington Optiwhite™ low iron, high-visible-light transmission glass laminated with an intumescent interlayer.

Impact Safety Resistance:  ANSI Z97.1 and CPSC 16CFR1201 (Cat. I and II).

Adjust list of properties below to suit Project -- these are listed in tabular form delete those columns not used.

Properties Interior Glazing

| Fire-Rating | 60 Minutes | 120 Minutes |
| --- | --- | --- |
| Manufacturer’s designation | 60-201 | 120-60 |
| Glazing type | Single | Single |
| Nominal Thickness | 1-1/16” (27mm) | 1-7/8” (47mm) |
| Weight in lbs/sf | 12.5 | 21.9 |
| Daylight Transmission | 86% | 81% |
| Sound Transmission Coefficient | 44dB | 46dB |

Note:  For bullet resistance requirements, please see the Fireframes Heat Barrier Series bullet resistant CSI specifications.

Logo:  Each piece of fire-rated glazing shall be labeled with a permanent logo including name of product, manufacture, testing laboratory (UL), fire rating period, safety glazing standards, and date of manufacture.

Glazing Accessories: Manufacturer’s standard compression gaskets, spacers, setting blocks and other accessories necessary for a complete installation.

MATERIALS – STEEL FRAMES

Adjust list of minutes below to suit Project.

Steel Framing System [60 min.] [120 min]:

Frame:

[Steel] profiled formed tubing permanently joined with steel bolts, mechanical joint connector

Insulation:  Insulate framing system against effects of fire, smoke, and heat transfer from either side. Insulate profiled steel tubing using a shell construction that incorporates Promatect-H intermediate interlayer. Firmly pack perimeter of framing system to rough opening with mineral wool fire stop insulation or appropriately rated intumescent sealant.

Steel Glazing Beads:  Extruded steel beads with dimensions recommended by manufacturer to securely hold glazing material in place.

Fasteners:  Type recommended by manufacturer

Glazing Accessories:

Set Pilkington Pyrostop glass using calcium silicate, or setting blocks.

Intumescent tape

Alignment Clamp Strip Assembly-temporary clamping strips for alignment of Pilkington Pyrostop® are required. Components provided include 4” long gasketed temporary clamping strip, M4 threaded rods (4”) in length, wing nuts, and washers.

Glazing Gaskets, Compounds and tapes:

Glaze Pilkington Pyrostop glass with approved EPDM glazing gaskets and [closed cell PVC tape], or [pure silicone sealant].

Ceramic tape

Butt-joint sealant, Pilkington Pyrostop® Sealant 1 (Ceresit 3B / Unibond 3B) MUST BE USED (no exceptions or substitutions) at all butt-glazed glass edges.

FABRICATION

Furnish interior frame assemblies “K-D” (or welded upon request).

When necessary, splice frames too large for shop fabrication or shipping or to fit in available building openings.

Fit with suitable fasteners.

Field glaze frame assemblies.

Fabrication Dimensions:  Fabricate fire rated assembly to field dimensions.

Obtain approved Shop Drawings prior to fabrication.

FINISHES, GENERAL

Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes see [Fireframes® Heat Barrier Series] [Fireframes Aluminum Series] specifications for available finishes detail.

Finish frames after assembly.

Appearance of Finished Work:  Variations in appearance of abutting or adjacent pieces are acceptable.  Noticeable variations in the same piece are not acceptable.

EXECUTION

EXAMINATION

Examine substrates and members to which the work of this section attaches or adjoins prior to frame installation.

Provide openings plumb, square and within allowable tolerances.

The manufacturer recommends 3/8 inch shim space at all walls

Notify Architect of any conditions which jeopardize the integrity of the proposed fire wall system.

Do not proceed until such conditions are corrected.

INSTALLATION

See [Fireframes Heat Barrier] [Fireframes Aluminum Series] Installation Manual

REPAIR AND TOUCH UP

Limited to minor repair of small scratches. Use only manufacturer’s recommended products.

Such repairs shall match original finish for quality or material and view.

Remove and replace glass that is broken, chipped, cracked, abraded, or damaged.

PROTECTION AND CLEANING

Protect glass from damage immediately after installation by attaching crossed streamers to framing held away from glass.  Do not apply markers to glass surface.  Remove nonpermanent labels, and clean surfaces.

Do not clean with astringent cleaners. Use a clean “grit free” cloth and a small amount of mild soap and water or mild detergent.

Do not use any of the following:

Steam jets

Abrasives

Strong acidic or alkaline detergents, or surface-reactive agents

Detergents not recommended in writing by the manufacturer

Do not use any detergent above 77 degrees F

Organic solvents including but not limited to those containing ester, ketones, alcohols, aromatic compounds, glycol ether, or halogenated hydrocarbons.

Metal or hard parts of cleaning equipment must not touch the glass surface

Reference manufacturer’s glazing and handling guidelines for special instructions on Pilkington Pyrostop® Line (butt-joint).

Protect glass from contact with contaminating substances resulting from construction operations, including weld splatter.  If, despite such protection, contaminating substances do come into contact with glass, remove them immediately as recommended by glass manufacturer.

Modify paragraph below to suit Project.

Wash glass on both exposed surfaces in each area of Project not more than four days before date scheduled for inspections that establish date of Substantial Completion.  Wash glass as recommended by glass manufacturer.

END OF SECTION